## Sheet1
District | Building | Date of Test | Low Range (ppb) | High Range (ppb) | Remediation Plan | Updated Water Quality Status | Date of Remediation Completion
Cocalico SD | High School | 2/26/19 & 3/5/2019 | 0.0001 | 0.041 | Flushed and/or replaced | Pass | 3/8 & 3/27/2019
Cocalico SD | Reamstown Elementary | 2019-03-05 | 0.007 | 0.469 | Flushed and/or replaced | Pass | 3/5, 3/8, & 3/27/2019
Cocalico SD | Adamstown Elementary | 2019-03-22 | 0.0001 | 0.0222 | Flushed | Pass | 2019-03-27
Allegheny-Clarion Valley SD | Elementary School | 2019-04-19 | 0 | 65.8 | Shut off. Posted signs. Provided bottled water. | N/A | N/A
Allegheny-Clarion Valley SD | Jr/Sr High School | 2019-04-19 | 0 | 71.8 | Shut off. Posted signs. Provided bottled water. | N/A | N/A
Bellefonte ASD | Pleasant Gap Elementary | 2019-04-04 | 0 | 23.6 | Removed from service | N/A | 2019-04-08
Smethport ASD | Smethport Elementary | 2018-11-30 | 0 | 62.3 | Disconnected | N/A | 2019-01-01
Smethport ASD | Smethport High School | 2019-11-30 | 0 | 41.4 | Re-test | Pass | 2019-01-01
Jefferson County DuBois AVTS (Jeff Tech) | Main | 2019-03-16 | 0 | 419 | "Do Not Drink" Sign | N/A | 2019-05-17
Jefferson County DuBois AVTS (Jeff Tech) | Annex | 2019-04-09 | 0 | 163 | "Do Not Drink" Sign | N/A | 2019-05-17
Carbon Lehigh IU 21 | Lehigh County Enhanced Autism BS-5 | 2019-03-16 | 0 | 18 | Replaced aerator | N/A | N/A
Carbon Lehigh IU 21 | Lehigh County Enhanced Autism BS-7 | 2019-03-16 | 0 | 564 | Replaced aerator | N/A | N/A
Carbon Lehigh IU 21 | Carbon Learning and Achievement School BS-8 | 2019-03-16 | 0 | 16 | Replaced faucet | N/A | N/A
Carbon Lehigh IU 21 | Life House BS-1 | 2019-03-16 | 0 | 17 | Installed filter | N/A | N/A
Carbon Lehigh IU 21 | Life House BS-2 | 2019-03-16 | 0 | 58 | Decommissioned | N/A | 2019-04-12
Carbon Lehigh IU 21 | Life House KS-1 | 2019-03-16 | 0 | 55 | Installed filter | N/A | N/A
End of first quarterly report
North Hills School District | McIntyre Elementary School | 2018-10-09 | 0 | 24.5 | Taken out of service | N/A | 2018-10-09
North Hills School District | North Hills Middle School | 2018-10-09 | 0 | 19.4 | Taken out of service on one source. Filter installed on the other source. | <1 ppb | 2019-01-29
North Hills School District | West View Elementary School | 2018-10-09 | 0 | 46.9 | Taken out of service | N/A | 2018-10-09
Governor Mifflin SD | Mifflin Park Elementary School | 2019-05-01 | 0 | 0.044 | Hose splitter on the hose bib was removed. | 0.003 | 2019-05-08
Lancaster-Lebanon IU 13 | Fairland School | 2019-05-15 | 0.002 | 0.058 | Posted non-potable water notice signs. Provided bottled water. Replacing pipes & supply valves from fixtures to main line. | N/A | N/A
Lancaster-Lebanon IU 13 | Community School West | 2019-05-15 | 0.004 | 0.215 | Posted non-potable water notice signs. Provided bottled water. Replacing pipes & supply valves from fixtures to main line. | N/A | N/A
Lancaster-Lebanon IU 13 | Mulberry Street School | 2019-05-17 | <.001 | 0.015 | At failed sink, posted non-potable water notice; bottled water is provided; landlord replaced fittings & supply valve. | Passed | 2019-06-21
Lincoln Intermediate Unit #12 | Franklin Learning Center | 2019-01-31 | 0.002 | 0.03 | Permanent and interim | Pending | 2020-02-01
Lincoln Intermediate Unit #12 | York Learning Center | 2019-02-06 | 0.002 | 0.087 | Permanent and interim | Pending | 2020-02-01
North Penn School District | York Avenue Elementary | 2019-01-10 | <2.5 | 30.09 | Replaced Fixture | <15ppb | 2019-04-11
North Penn School District | Knapp Elementary | 2019-01-15 | <2.5 | 64.5 | Replaced Fixtures | <15ppb | 2019-04-11
North Penn School District | North Penn High School | 2019-01-21 | <2.5 | 15.65 | Replaced Hose Outlet | <15ppb | 2019-04-11
North Penn School District | Gwynedd Square Elementary | 2019-01-17 | <2.5 | 24.29 | Replaced Fixtures | <15ppb | 2019-04-11
North Penn School District | Pennbrook Middle School | 2019-01-24 | <2.5 | 19.75 | Replaced aerator | <15ppb | 2019-04-11
North Penn School District | Gwyn Nor Elementary | 2019-01-11 | <2.5 | 20.42 | Replaced Fixture | <15ppb | 2019-04-11
North Penn School District | Oak Park Elementary | 2019-01-10 | <2.5 | 41.68 | Replaced Fixture | <15ppb | 2019-04-11
North Penn School District | Pennfield Middle School | 2019-01-22 | <2.5 | 43.55 | Remove from service | 23.34 (Flush) | 2019-05-14
Southern York County School District | Shrewsbury Elementary | 2019-06-04 | 2.9 | 16 | Shut off. Posted signs. | 90th | 2019-06-11
Dauphin County Tech School |  | 2019-04-09 | >1.0 | 144 | Removed from service. Flushed or replaced. | N/A | N/A
Dauphin County Tech School |  | 2019-06-07 | >1.0 | >1.0 | Re-test | Pass | 2019-06-07
Mid Valley School District | Secondary Center | 2019-06-20 | 1 | 17.1 | Shutt off. Out of service signs posted. Flushed and replaced aerator. | N/A | N/A
Milton Area School District | Baugher Elementary | 2019-02-26 | 10 | 18 | Replace fountain | Below 15 | 2019-05-07
Bethlehem Area Vocational Technical School | Main building | 2019-06-17 | 0 | 97 | Source Sample only, Install new drinking fountain retest. | <1 | 2019-08-09
Bethlehem Area Vocational Technical School | Main building | 2019-06-17 | 0 | 247 | Source Sample only, reinstall soup kettle flush and retest. | Reinstalled Fixture, First draw sample tested 22 ug/l and sample after 15 second flush was <1. Hung sign on wall stating 15 second purge before use. | 2019-08-09
Columbia-Montour Area VTS | Columbia-Montour Area VTS | 2019-03-27 | ND | 0.73 | Disable source / Test at wall to determine if the issue is with the supply line or fixture / Replace fixture of eliminate fixture depending upon result. Lead filter s installed. Awaiting re-test results. | <.001 mg/l | 2019-07-31
Jersey Shore Area School District | Jersey Shore Senior High School | 2019-05-03 | 0.015 | 7.3 | Install low lead fixtures | 0.0093 | 2019-08-19
Jersey Shore Area School District | Jersey Shore Middle School | 2019-05-01 | 0.022 | 0.13 | Install low lead fixtures | 0.0034 | 2019-08-19
Jersey Shore Area School District | Jersey Shore Elementary School | 2019-05-12 | 0.024 | 0.024 | Flushed and re-tested | 0.002 | 2019-07-18
Jersey Shore Area School District | Avis Elementary School | 2019-05-02 | 0.023 | 3.6 | Install low lead fixtures | 0.0044 | 2019-08-19
Jersey Shore Area School District | Salladasburg Elementary School | 2019-05-03 | 0.14 | 0.5 | Install low lead fixtures | 0.0012 | 2019-08-19
Jersey Shore Area School District | District Service Center | 2019-05-03 | 0.026 | 0.13 | Install low lead fixtures | 0.00015 | 2019-08-09
Benton Area School District | Middle/High School (Backflow preventer) | 2019-04-02 | 18 | 18 | Conduct additional testing in warmer period (July-August). Backflow Preventer Maintenance. Monitor water usage and flush low-use lines. Work with water provider. | 1.6 | 2019-07-23
Oley Valley School District | Middle School | 2018-10-24 | <1 | 27 | Clean/replaced aerator | Pass | 2018-12-18
Oley Valley School District | Elementary School | 2018-10-24 | <1 | 15 | Flushed/cleaned aerator | Pass | 2018-12-18
Oley Valley School District | High School | 2018-10-24 | <1 | 59 | Replaced piping | Pass | 2018-12-18
End of second quarterly report
Abington School District | Rydal East Elementary | 2019-04-30 | 0 | 225 | Removed From Service and Replaced Fixture | Pass | 2029-07-31
Abington School District | Willow Hill Elementary | 2019-04-16 | 0 | 512 | Removed From Service and Replaced Fixture | Pass | 2019-05-17
Abington School District | Senior High | 2019-05-08 | 0 | 163 | Removed From Service and Replaced Fixture | Pass | 2019-05-17
Abington School District | Junior High | 2019-05-01 | 0 | 65 | Removed From Service and Replaced Fixture | Pass | 2019-07-31
Abington School District | Administration | 2019-05-09 | 0 | 720 | Removed From Service and Replaced Fixture | Pass | 2019-06-17
Clarion-Limestone Area School District | C-L Elementary School | 2019-09-05 | 0 | 61 | Retest | Less than .005 | 2019-09-09
North Hills School District | NH Middle School | 2019-10-02 | 0 | 4.7 | Replace faucet and retest | N/A | 2019-11-01
Dover Area School District | Dover High School | 2019-08-21 | <005 | 0.025 | Replaced bubbler | Pass | 2019-10-11
Dover Area School District | North Salem Elementary | 2019-08-21 | <005 | 0.018 | Replaced sprayer | Pass | 2019-10-11
Dover Area School District | North Salem Elementary | 2019-08-21 | <005 | 0.016 | Replaced faucet | Pass | 2019-10-11
Dover Area School District | Weigelstown Elementary | 2019-08-21 | <005 | 0.02 | Installed lead filter | Pass | 2019-10-11
Dover Area School District | Leib Elementary | 2019-08-21 | <005 | 0.019 | Replaced faucet | Pass | 2019-10-11
Dover Area School District | Leib Elementary | 2019-08-21 | <005 | 0.034 | Replaced faucet | Pass | 2019-10-11
Dover Area School District | Dover Intermediate School | 2019-08-21 | <005 | 0.057 | Removed From Service | Pass | 2019-10-11
Dover Area School District | Dover Intermediate School | 2019-08-21 | <005 | 0.018 | Replaced faucet | Pass | 2019-10-11
Centennial School District | Davis E.S. | 2019-05-11 | 6.9 | 130 | Replaced faucet | Below 15 ppb | 2019-10-05
Centennial School District | Davis E.S. | 2019-05-11 | 6.1 | 16 | Replaced Aerator | Non-Detect | 2019-10-05
Centennial School District | Willow Dale E.S. (Ext.) | 2019-05-18 | 0 | 360 | Non-Pot Water Sign | N/A | 2019-10-05
Centennial School District | Willow Dale E.S. | 2019-05-18 | 3.8 | 18 | Replaced faucet | Non-Detect | 2019-10-05
Centennial School District | Klinger M.S. | 2019-05-11 | 3 | 86 | Replaced faucet | Non-Detect | 2019-10-05
Centennial School District | Klinger M.S. (Ext.) | 2019-05-11 | 0 | 470 | Non-Pot Water Sign | N/A | 2019-10-05
Centennial School District | Log College M.S. | 2019-05-18 | 2.3 | 33 | Replaced faucet | Non-Detect | 2019-10-05
Centennial School District | Log College M.S. | 2019-05-18 | 6.9 | 43 | Replaced faucet | Non-Detect | 2019-10-05
Centennial School District | Log College M.S.(Ext.) | 2019-05-18 | 0 | 24 | Non-Pot Water Sign | N/A | 2019-10-05
Centennial School District | Log College M.S. (Ext.) | 2019-05-18 | 0 | 24 | Non-Pot Water Sign | N/A | 2019-10-05
Centennial School District | William Tennent H.S. | 2019-05-18 | 4.4. | 16 | Replaced faucet | Non-Detect | 2019-10-05
Centennial School District | William Tennent H.S. (Ext.) | 2019-05-18 | 0 | 49 | Non-Pot Water Sign | N/A | 2019-10-05
Centennial School District | William Tennent H.S. | 2019-05-18 | 6 | 18 | Replaced faucet | Non-Detect | 2019-10-05
Centennial School District | District Admin. Bldg. | 2019-05-18 | 14 | 48 | Cleaned Aerator | Non-Detect | 2019-10-05
Waynesboro Area School District | Waynesboro Area Middle School | 2019-10-28 | N/A | 17 | Water cooler turned off and closed. Unit will be replaced and water retested on 11/11/19. | N/A | N/A
Waynesboro Area School District | Fairview Elementary School | 2019-11-01 | N/A | 89 | Water cooler turned off and closed. Unit will be replaced and water retested on 11/11/19. | N/A | N/A
Parkland School District | Troxell Building | 2019-09-19 | <.001 | 0.016 | Removed bathroom from service | Pending | 2019-10-22
Bloomsburg Area School District | Beaver Main Elementary School | 2019-06-07 | 16.2 | 16.2 | Replaced old piping | 8.88 | 2019-08-22
Bloomsburg Area School District | W.W. Evans Elementary School | 2019-06-24 | 16 | 16 | Replaced bubbler & aerator | 1.96 | 2019-09-10
Bloomsburg Area School District | W.W. Evans Elementary School | 2019-06-24 | 15.6 | 15.6 | Replaced bubbler & aerator | <1 | 2019-09-10
Bloomsburg Area School District | Bloomsburg High School | 2019-05-24 | 60.3 | 60.3 | Replaced Aerator | 2.96 | 2019-09-11
East Stroudsburg Area School District | Middle Smithfield Elementary School | 2019-06-06 | 9 | 16.5 | Replaced sink faucet | Below required/Pass | 2019-07-26
East Stroudsburg Area School District | Middle Smithfield Elementary School | 2019-06-10 | 9.3 | 28 | Replaced sink faucet | Below required/Pass | 2019-07-31
Allentown School District | Harrison-Morton MS | 2019-08-27 | <1 | 32 | Flushed and/or replaced | 8 | 2019-09-23
Allentown School District | Dieruff HS | 2019-08-27 | <1 | 22 | Flushed and/or replaced | 9 | 2019-09-23
Allentown School District | Mosser ES | 2019-08-27 | <1 | 86 | Flushed and/or replaced | <1 | 2019-10-01
Allentown School District | Washington ES | 2019-08-27 | <1 | 33 | Flushed and/or replaced | 3 | 2019-09-23
Allentown School District | Ramos ES | 2019-08-27 | <1 | 20 | Flushed and/or replaced | 2 | 2019-09-23
Allentown School District | Muhlenberg ES | 2019-08-27 | <1 | 32 | Flushed and/or replaced | 13 | 2019-09-23
Allentown School District | Union Terrace ES | 2019-08-27 | <1 | 19 | Flushed and/or replaced | 2 | 2019-09-23
Allentown School District | Union Terrace ES | 2019-08-27 | <1 | 16 | Flushed and/or replaced | 5 | 2019-09-23
Allgheny Intermediate Unit | The Pathfinder School | 2019-04-02 | <1.0 | 71.8 | Sign posted/fountain capped/new fixture and filter installed
Mastery Charter Schools | Douglass Elementary | 2019-04-27 | 18 | 3750 | Shut off all drinking fountains. Water has been brought in for drinking in the building. | N/A | 2019-04-30
Mastery Charter Schools | Cleveland | 2019-04-27 | 289 | 289 | Fountains turned off and sinks have signs for not drinking on them. | N/A | 2019-04-30
Mastery Charter Schools | Lenfest | 2019-04-27 | 73.5 | 73.5 | Sink has sign placed over it | N/A | 2019-04-30
Mastery Charter Schools | Mann Elementary | 2019-04-27 | 55.3 | 148 | Sink has sign placed over it | N/A | 2019-04-30
Mastery Charter Schools | Pastorius | 2019-04-27 | 12 | 757 | Installed signs over sinks. | N/A | 2019-04-30
Mastery Charter Schools | Pickett | 2019-04-27 | 12.61 | 174 | Took fountains out of service and placed signs over sinks. | N/A | 2019-04-30
Mastery Charter Schools | Shoemaker | 2019-04-27 | 14.6 | 14.6 | Took fountain out of service | N/A | 2019-04-30
Mastery Charter Schools | Gratz | 2019-04-27 | 14.4 | 39.1 | Took fountain out of service | N/A | 2019-04-30
End of Third Quarterly Report
Jefferson County DuBois AVTS (Jeff Tech) | Main | 2019-11-16 | 0 | 19 | Do Not Drink Sign | N/A | 2019-12-05
Jefferson County DuBois AVTS (Jeff Tech) | Annex | 2019-11-16 | 0 | 23 | Do Not Drink Sign | N/A | 2019-12-05
Riverview School District | Riverview Jr/Sr HS | 2018-10-08 | <1.00 | 2.42 | Shut down water fountain and replaced the filter. Re tested and found the lead levels dropped to 1 | 1.17 | 2018-10-29
Riverview School District | Riverview Jr/Sr HS | 2018-09-27 | <1.00 | 3.03 | Closed the fountain. Changed filter and cleaned the out aerator. Flushed the system. Re-tested. | <1.00 | 2018-11-07
Riverview School District | Riverview Jr/Sr HS | 2018-09-25 | <1.00 | 1.33 | Closed the fountain. Cleaned the screen on the outlet and changed the filter. | <1.00 | 2018-11-07
Riverview School District | Riverview Jr/Sr HS | 2018-09-26 | <1.00 | 1.58 | Shut the sink down. Flushed the sink. Changed the aerator. Re- tested. | 1.49 | 2018-11-07
Riverview School District | Riverview Jr/Sr HS | 2018-09-26 | <1.00 | 3.08 | Shut down the sink. Flushed the sink. Changed the aerator. Re-tested. | 1.34 | 2018-11-07
Riverview School District | Riverview Jr/Sr HS | 2018-09-28 | <1.00 | 1.7 | Shut down the sink. Flushed the sink. Changed the aerator. Re-tested | 1.16 | 2018-11-07
Riverview School District | Riverview Jr/Sr HS | 2018-09-29 | <1.00 | 1.08 | Shut down the sink. Flushed the line and changed the aerator. Re-tested. | <1.00 | 2018-11-07
Riverview School District | Tenth Street Elementary | 2018-09-18 | 2.49 | 3.55 | Shut down the water fountain. Changed the filters and cleaned the aerator. Re-tested. | <1.00 | 2018-11-15
Riverview School District | Tenth Street Elementary | 2018-09-18 | 1.44 | 2.08 | Shut down the water fountain. Flushed the line. Changed the filter and cleaned the aerator. Re-tested. | <1.00 | 2018-11-15
Riverview School District | Tenth Street Elementary | 2018-09-23 | <1.00 | 7.54 | Shut down the sink. Flushed the water line. Installed a new aerator. Re-tested. | <1.00 | 2018-11-15
Riverview School District | Verner Elementary | 2018-09-18 | <1.00 | 3.19 | Shut down the sink. Flushed the water line and installed a new aerator. Re-tested. | 2.79 | 2018-10-31
Fort Cherry School District | Elementary | 2019-04-04 | 1.7 | 6.8 | New faucet installed. | 1.7 | 2019-07-17
Fort Cherry School District | Elementary | 2019-04-04 | 1 | 10.2 | New faucet and filter installed. | 1 | 2019-12-17
North Pocono School District | NP Middle School | 2019-09-25 | 0.001 | 0.0244 | Following DEP | The district is in compliance after resample | N/A
Smethport ASD | Smethport Elementary | 2019-12-09 | 0 | 0.129 | Disconnect the fixture. Al fixtures of this type have been removed. | N/A | 2019-12-31
Pittsburgh Public Schools | Pittsburgh Brookline PreK-8; Demountable Classroom | 5/9/219 | 0 | 15 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 3.8 | 2019-05-31
Pittsburgh Public Schools | Pittsburgh Carrick High School- Nurse's Office Sink Faucets | 2019-04-18 | 0 | 36.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 11.4 | 2019-06-04
Pittsburgh Public Schools | Pittsburgh Carrick High School- Home EC Kitchen Faucet | 2019-04-18 | 0 | 32.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 8.73 | 2019-06-04
Pittsburgh Public Schools | Pittsburgh Clayton Academy | 2019-06-12 | 0 | 15.8 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-07-17
Pittsburgh Public Schools | Pittsburgh Crescent Early Childhood Center | 2019-02-16 | 0 | 82.8 | Fixture taken out of service. | 39.7 | 2019-02-16
Pittsburgh Public Schools | Pittsburgh Greenfield PreK-8 | 2019-04-09 | 0 | 29.4 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 23.7 | 2019-04-24
Pittsburgh Public Schools | Pittsburgh King PreK-8; Classroom Faucets | 2019-04-16 | 0 | 2.7 First Draw 42.5 Second Draw | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2.27 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh King PreK-8; Classroom Faucets | 2019-04-16 | 0 | 16.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2.31 | 2019-05-23
Pittsburgh Public Schools | Pittsburgh King PreK-8; Classroom Faucets | 2019-04-16 | 0 | 34.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 7.78 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh King PreK-8; Classroom Faucets | 2019-04-16 | 0 | 46 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 13.4 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh King PreK-8; Water Fountain Attached to Sink | 2019-04-16 | 0 | 22 | Water fountain removed and capped. | 7.15 | 4/16/2019- Second Draw
Pittsburgh Public Schools | Pittsburgh Langley K-8; Classroom Faucets | 2019-05-18 | 0 | 525 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 4.11 | 2019-06-07
Pittsburgh Public Schools | Pittsburgh Langley K-8; Classroom Faucets | 2019-05-18 | 0 | 36.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-06-07
Pittsburgh Public Schools | Pittsburgh Lincoln PreK-5; Nurse's Office Sink Faucets | 2019-05-02 | 0 | 18.8 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 6.22 | 2019-05-14
Pittsburgh Public Schools | Pittsburgh Lincoln PreK-5; Classroom Faucets | 2019-05-02 | 0 | 69.3 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 14.2 | 2019-05-14
Pittsburgh Public Schools | Pittsburgh Lincoln PreK-5; Classroom Faucets | 2019-05-02 | 0 | 27.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 11.8 | 2019-05-14
Pittsburgh Public Schools | Pittsburgh Lincoln PreK-5; Miscellaneous sinks | 2019-05-02 | 0 | 50.2 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 26.1 | 2019-05-14
Pittsburgh Public Schools | Pittsburgh Lincoln PreK-5; Miscellaneous sinks | 2019-05-02 | 0 | 188 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 10.6 | 2019-05-14
Pittsburgh Public Schools | Pittsburgh Linden K-5; Miscellaneous Sinks | 2019-05-14 | 0 | 21.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 5.37 | 2019-06-05
Pittsburgh Public Schools | Pittsburgh Linden K-5; Miscellaneous Sinks | 2019-05-14 | 0 | 64.2 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 18.6 | 2019-06-05
Pittsburgh Public Schools | Pittsburgh Manchester PreK-8; Classroom Faucets | 2019-04-23 | 0 | 38 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 8.24 | 2019-05-03
Pittsburgh Public Schools | Pittsburgh Manchester PreK-8; Miscellaneous Sinks | 2019-04-23 | 0 | 20.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 6.74 | 2019-05-03
Pittsburgh Public Schools | Pittsburgh Manchester PreK-8; Classroom Faucets | 2019-04-23 | 0 | 17.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 1.14 | 2019-05-15
Pittsburgh Public Schools | Pittsburgh Manchester PreK-8; Water Fountain Attached to Sink | 2019-04-23 | 0 | 21.7 | Water fountain removed and capped. | 3.24 | 4/23/2019- Second Draw
Pittsburgh Public Schools | Pittsburgh Mentessori PreK-5 | 2019-02-16 | 0 | 33.7 | Fixture not utilized. | 7.63 | 2019-02-27
Pittsburgh Public Schools | Pittsburgh Online Academy (South Annex); Classroom Faucets | 2019-06-18 | 0 | 18.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 6.49 | 2019-06-27
Pittsburgh Public Schools | Pittsburgh Online Academy (South Annex); Water Fountain with Cooler | 2019-06-18 | 0 | 106 | Fixture was taken out of service. | 74.7 | 2019-06-18
Pittsburgh Public Schools | Pittsburgh Online Academy (South Annex); Water Fountain with Cooler | 2019-06-18 | 0 | 45.1 | Fixture was taken out of service. | 6.09 | 2019-06-18
Pittsburgh Public Schools | Pittsburgh Online Academy (South Annex); Classroom Faucets | 2019-06-18 | 0 | 38.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 14 | 2019-06-27
Pittsburgh Public Schools | Pittsburgh Online Academy (South Annex); Classroom Faucets | 2019-06-18 | 0 | 15 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 7.72 | 2019-06-27
Pittsburgh Public Schools | Pittsburgh Perry High School | 2019-06-01 | 0 | 22.5 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 3.31 | 2019-07-09
Pittsburgh Public Schools | Pittsburgh Schenley Field House | 2019-04-30 | 0 | 25.9 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 12.4 | 2019-05-31
Pittsburgh Public Schools | Pittsburgh Sterrett 6-8 | 2019-06-11 | 0 | 24.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-07-11
Pittsburgh Public Schools | Pittsburgh Sunnyside PreK-8 | 2019-04-10 | 0 | 16.5 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-05-02
Pittsburgh Public Schools | Pittsburgh Weil PreK-5; Classroom Faucets | 2019-04-03 | 0 | 15.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 3.27 | 2019-04-13
Pittsburgh Public Schools | Pittsburgh Weil PreK-5; Classroom Faucets | 2019-04-03 | 0 | 60.6 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 18.2 | 2019-04-13
Pittsburgh Public Schools | Pittsburgh Weil PreK-5; Classroom Faucets | 2019-04-03 | 0 | 38.5 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 8.78 | 2019-04-13
Pittsburgh Public Schools | Pittsburgh Weil PreK-5; Miscellaneous Sinks | 2019-04-03 | 0 | 54.3 | A "Hand Wash Only- Do Not Drink From Faucet" sign was posted. | 17.2 | 2019-04-13
Pittsburgh Public Schools | Pittsburgh Westinghouse Academy 6-12; Nurses's Office Sink Faucets | 2019-04-06 | 0 | 19.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2.01 | 2019-04-27
Pittsburgh Public Schools | Pittsburgh Westinghouse Academy 6-12; Nurses's Office Sink Faucets | 2019-04-06 | 0 | 25.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-05-07
Pittsburgh Public Schools | Pittsburgh Westinghouse Academy 6-12; Classroom Faucets | 2019-04-06 | 0 | 17.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 1.09 | 2019-04-27
Pittsburgh Public Schools | Pittsburgh Westhinghouse Academy 6-12; Miscellaneous Sinks | 2019-04-06 | 0 | 15.9 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 14.5 | 2019-04-27
Pittsburgh Public Schools | Pittsburgh Westhinghouse Academy 6-12; Classroom Faucets | 2019-04-06 | 0 | 50.8 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 8.84 | 2019-04-27
Pittsburgh Public Schools | Pittsburgh Westinghouse Academy 6-12; Classroom Faucets | 2019-04-06 | 0 | 16 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 12.8 | 2019-04-27
Pittsburgh Public Schools | Pittsburgh Westinghouse Field House | 2019-04-10 | 0 | 16.9 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 9.82 | 2019-04-27
Pittsburgh Public Schools | Pittsburgh Administration Building; Office Sink Faucets | 2019-07-02 | 0 | 40.8 | Shut off fixture. Sign posted. | 26.9 | 2019-07-20
Pittsburgh Public Schools | Pittsburgh Administration Building; Office Sink Faucets | 2019-07-02 | 0 | 17.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 13.5 | 2019-07-20
Pittsburgh Public Schools | Pittsburgh Administration Building; Office Sink Faucets | 2019-07-02 | 0 | 20.5 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 5.88 | 2019-07-20
Pittsburgh Public Schools | Pittsburgh Administration Building; Office Sink Faucets | 2019-07-02 | 0 | 68.5 | Shut off fixture. Sign posted. | 19.3 | 2019-07-20
Pittsburgh Public Schools | Pittsburgh Allderdice High School- Classroom Faucets | 2019-04-16 | 0 | 15.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 10 | 2019-04-26
Pittsburgh Public Schools | Pittsburgh Allderdice High School- Classroom Faucets | 2019-04-16 | 0 | 16.2 | Shut off fixture. Sign posted. | 16.8 | 2019-05-01
Pittsburgh Public Schools | Pittsburgh Allegheny K-5/6-8; Classroom Faucets | 2019-05-04 | 0 | 16.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2.16 | 2019-05-15
Pittsburgh Public Schools | Pittsburgh Allegheny K-5/6-8; Water Fountain Bubbler | 2019-05-04 | 0 | 6.26 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 1.38 | 2019-05-15
Pittsburgh Public Schools | Pittsburgh Arsenal Pre K-5/6-8; Nurse's Office Sink Faucets | 2019-04-18 | 0 | 18.5 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 8.62 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh Aresenal Pre K-5/6-8; Classroom Faucets | 2019-04-18 | 0 | 67.4 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 7.3 | 2019-04-30
Pittsburgh Public Schools | Brashear South Hills 6-8; Classroom Faucets | 2019-04-27 | 0 | 140 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-05-04
Pittsburgh Public Schools | Brashear South Hills 6-8; Water Fountain with Cooler | 2019-04-27 | 0 | 30.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 1 | 2019-05-04
Pittsburgh Public Schools | Brashear South Hills 6-8; Classroom Faucets | 2019-04-27 | 0 | 119 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2 | 2019-05-04
Pittsburgh Public Schools | Pittsburgh CAPA- Classroom Faucets | 2019-05-25 | 0 | 33.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-06-06
Pittsburgh Public Schools | Pittsburgh CAPA- Classroom Faucets | 2019-05-25 | 0 | 35.1 | Shut off fixture. Sign posted. | 9.59 | 2019-06-06
Pittsburgh Public Schools | Pittsburgh Concord Pre K-5 | 2019-04-06 | 0 | 18.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-04-16
Pittsburgh Public Schools | Pittsburgh Conroy- Kitchen Faucets | 2019-05-11 | 0 | 20.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 1.77 | 2019-05-21
Pittsburgh Public Schools | Pittsburgh Conroy- Kitchen Faucets | 2019-05-11 | 0 | 39.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2.1 | 2019-05-21
Pittsburgh Public Schools | Pittsburgh Conroy- Kitchen Faucets | 2019-05-11 | 0 | 62.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-05-21
Pittsburgh Public Schools | Pittsburgh Dilworth Pre K-5; Classroom Faucets | 2019-04-06 | 0 | 16.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 3 | 2019-04-18
Pittsburgh Public Schools | Pittsburgh Dilworth Pre K-5; Classroom Faucets | 2019-04-06 | 0 | 20.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-04-18
Pittsburgh Public Schools | Pittsburgh Dilworth Pre K-5; Classroom Faucets | 2019-04-08 | 0 | 17.3 | Signage posted. | 2.3 | 4/8/2019- Second Draw
Pittsburgh Public Schools | Pittsburgh Grandview- Classroom Faucets | 2019-06-05 | 0 | 18.2 | Shut off fixture. Sign posted. | 75.3 | 2019-06-15
Pittsburgh Public Schools | Pittsburgh Grandview- Classroom Faucets | 2019-06-05 | 0 | 274 | Shut off fixture. Sign posted. | 107 | 2019-06-15
Pittsburgh Public Schools | Pittsburgh Grandview- Water Fountain without Cooler | 2019-06-05 | 0 | 21.5 | Fixture removed. | 2.35 | 6/5/2019- Second Draw
Pittsburgh Public Schools | Pittsburgh Grandview- Classroom Faucets | 2019-06-05 | 0 | 15.7 | Shut off fixture. Sign posted. | 23.8 | 2019-06-15
Pittsburgh Public Schools | Pittsburgh Grandview- Classroom Faucets | 2019-06-05 | 0 | 289 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 4.4 | 2019-06-15
Pittsburgh Public Schools | Greenway Classial-Gifted Center | 2019-06-08 | 0 | 349 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 2.56 | 6/8/2019- Second Draw
Pittsburgh Public Schools | Pittsburgh Liberty K-5 | 2019-06-05 | 0 | 16.2 | Shut off fixture. Sign posted. Replaced or removed assembly. | 31.9 | 2019-07-02
Pittsburgh Public Schools | Pittsburgh Minadeo Pre K-5; Teacher's Lounge Sinks | 2019-04-18 | 0 | 16 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh Minadeo Pre K-5; Classroom Faucets | 2019-04-18 | 0 | 36.3 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 13.7 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh Minadeo Pre K-5; Home Economics Faucets (with Cooking) | 2019-04-18 | 0 | 20.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 4.86 | 2019-05-09
Pittsburgh Public Schools | Pittsburgh Minadeo Pre K-5; Classroom Faucets | 2019-04-18 | 0 | 20.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 4.62 | 2019-04-30
Pittsburgh Public Schools | Pittsburgh Obama- Home Economics Room Not In Use | 2019-03-30 | 0 | 18.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-04-11
Pittsburgh Public Schools | Pittsburgh Obama- Home Economics Room Not In Use | 2019-03-30 | 0 | 15.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-04-11
Pittsburgh Public Schools | Pittsburgh Oliver- Classroom Faucets | 2019-06-13 | 0 | 110 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 9.65 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Sink Faucet (Culinary Arts- Not In Use) | 2019-06-13 | 0 | 104 | Shut off fixture. Sign posted. | 18.6 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Office Sink Faucets | 2019-06-13 | 0 | 31.3 | Shut off fixture. Sign posted. | 19.6 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Classroom Faucets | 2019-06-13 | 0 | 17.9 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 11.2 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Classroom Faucets | 2019-06-13 | 0 | 28.1 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 14.5 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Classroom Faucets | 2019-06-13 | 0 | 16.9 | Shut off fixture. Sign posted. | 97.8 | 2019-07-19
Pittsburgh Public Schools | Pittsburgh Oliver- Classroom Faucets | 2019-06-13 | 0 | 21.2 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 14.3 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Office Sink Faucets | 2019-06-13 | 0 | 81.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 8.96 | 2019-07-19
Pittsburgh Public Schools | Pittsburgh Oliver- Classroom Faucets | 2019-06-13 | 0 | 72.8 | Shut off fixture. Sign posted. | 44.7 | 2019-07-19
Pittsburgh Public Schools | Pittsburgh Oliver- Sink Faucet (Culinary Arts- Not In Use) | 2019-06-13 | 0 | 66 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 7.74 | 2019-06-25
Pittsburgh Public Schools | Pittsburgh Oliver- Sink Faucet (Culinary Arts- Not In Use) | 2019-06-13 | 0 | 101 | Shut off fixture. Sign posted. | 27.3 | 2019-07-19
Pittsburgh Public Schools | Pittsburgh Oliver- Sink Faucet (Culinary Arts- Not In Use) | 2019-06-13 | 0 | 36.6 | Shut off fixture. Sign posted. | 17.4 | 2019-07-19
Pittsburgh Public Schools | Pittsburgh Oliver- Sink Faucet (Culinary Arts- Not In Use) | 2019-06-13 | 0 | 58.9 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 3.14 | 2019-07-19
Pittsburgh Public Schools | Pittsburgh Schiller | 2019-08-14 | 0 | 65 | Shut off fixture. Sign posted. | 65 | 2019-08-17
Pittsburgh Public Schools | Pittsburgh Spring Garden ECC- Classroom Faucets | 2019-02-16 | 0 | 20.5 | Shut off fixture. Sign posted. | 21 | 2019-03-05
Pittsburgh Public Schools | Pittsburgh Spring Garden ECC- Classroom Faucets | 2019-02-16 | 0 | 69.1 | Shut off fixture. Sign posted. | 77.4 | 2019-03-05
Pittsburgh Public Schools | Pittsburgh Student Achievement Center- Water Fountain Bubbler (Ceramic or Porcelin) | 2019-06-15 | 0 | 31 | Shut off fixture. Sign posted. | 17.4 | 2019-06-15
Pittsburgh Public Schools | Pittsburgh Student Achievement Center- Office Sink Faucets | 2019-06-15 | 0 | 15.6 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 4.83 | 2019-06-15
Pittsburgh Public Schools | Pittsburgh Student Achievement Center- Classroom Faucets | 2019-06-15 | 0 | 15.7 | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | 10.1 | 2019-06-15
Pittsburgh Public Schools | Pittsburgh Whittier K-5 | 2019-06-01 | 0 | 1.67 First Draw 17.4 Second Draw | Various including shutting off fixture, posting signage, removing/replacing aerator, replacing with new sink assembly, or removing sink altogether. | <1.00 | 2019-06-18
Scranton School District | George Bancroft | 2019-03-04 | 0.017 | 0.509 | Turn off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | McNicols Plaza | 2019-03-04 | 0.056 | 0.025 | Turn off fountain and post appropriate signage | Turned off | 2020-01-09
Scranton School District | William Prescott | 2019-03-04 | 0.018 | 0.04 | Turn off fountain and post appropriate signage | Turned off | 2020-01-09
Scranton School District | Scranton High School | 2019-03-04 | 0.022 | 0.016 | Turn off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | West Scranton Intermediate | 2019-03-04 | 0.017 | 0.0305 | Turn off fountain and post appropriate signage | Turned off | 2020-01-09
Scranton School District | West Scranton Intermediate | 2019-03-04 | 0.029 | 0.052 | Post appropriate signage | Unchanged | 2020-01-09
Scranton School District | West Scranton Intermediate | 2019-03-04 | 0.028 | 0.71 | Post appropriate signage | Unchanged | 2020-01-09
Scranton School District | William Prescott | 3/4/219 | 0.018 | 0.018 | Turn off fountain and post appropriate signage | Turned off | 2020-01-09
Scranton School District | William Prescott | 2020-01-14 | 0.021 | 0.021 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | William Prescott | 2020-01-14 | 0.022 | 0.022 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | William Prescott | 2020-01-14 | 0.079 | 0.079 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | William Prescott | 2020-01-14 | 0.056 | 0.056 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | William Prescott | 2020-01-14 | 0.18 | 0.18 | Post appropriate signage | Post appropriate signage | 2020-01-14
Scranton School District | William Prescott | 2020-01-14 | 0.045 | 0.045 | Turn off sink and post appropriate signage | Turned off | 2020-01-21
Scranton School District | William Prescott | 2020-01-20 | 0.013 | 0.013 | Turn off sink and post appropriate signage | Turned off | 2020-01-21
Scranton School District | William Prescott | 2020-01-17 | 0.005 | 0.005 | Turn off sink and post appropriate signage | Turned off per principal directive | 2020-01-17
Scranton School District | John G. Whittier | 2020-01-13 | 0.0162 | 0.0162 | Post appropriate signage | Post appropriate signage | 2020-01-14
Scranton School District | Scranton High School | 2019-03-04 | 0.022 | 0.022 | Turn off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | Stadium | 2020-01-13 | 0.128 | 0.128 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | Stadium | 2020-01-13 | 0.0577 | 0.0577 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | Stadium | 2020-01-13 | 0.0551 | 0.0551 | Turn off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | West Intermediate | 2019-03-04 | 0.017 | 0.017 | Turn off fountain and post appropriate signage | Turned off | 2020-01-09
Scranton School District | West Intermediate | 2019-03-04 | 0.029 | 0.029 | Turn off fountain and post appropriate signage | Turned off | 2020-01-17
Scranton School District | West Intermediate | 2019-03-04 | 0.028 | 0.028 | Post appropriate signage | Unable to shut off/no shut off valve | 2020-01-09
Scranton School District | West Intermediate | 2020-01-13 | 0.569 | 0.569 | Turn off sink and post appropriate signage | Turned off | 2020-01-21
Scranton School District | West Intermediate | 2020-01-13 | 0.0798 | 0.0798 | Turn off sink and post appropriate signage | Turned off | 2020-01-21
Scranton School District | Neil Armstrong | 2020-01-09 | 0.016 | 0.016 | Turn off sink and post appropriate signage | Turned off | 2020-01-16
Scranton School District | Neil Armstrong | 2020-01-09 | 0.215 | 0.215 | Turn off sink and post appropriate signage | Turned off | 2020-01-16
Scranton School District | Neil Armstrong | 2020-01-09 | 0.101 | 0.101 | Turn off sink and post appropriate signage | Turned off | 2020-01-16
Scranton School District | Neil Armstrong | 2020-01-09 | 0.205 | 0.205 | Turn off sink and post appropriate signage | Turned off | 2020-01-16
Scranton School District | Neil Armstrong | 2020-01-09 | 0.2 | 0.2 | Turn off sink and post appropriate signage | Turned off | 2020-01-16
Scranton School District | George Bancroft | 2019-03-04 | 0.017 | 0.017 | Turn off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | George Bancroft | 2020-01-09 | 0.03 | 0.03 | Turned off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | George Bancroft | 2020-01-09 | 0.018 | 0.018 | Appropriate signage | Appropriate signage | 2020-01-09
Scranton School District | George Bancroft | 2020-01-09 | 0.022 | 0.022 | Turned off sink and post appropriate signage | Turned off | 2020-01-17
Scranton School District | McNicols Plaza | 2020-01-09 | 0.016 | 0.016 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | McNicols Plaza | 2020-01-09 | 0.093 | 0.093 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | McNicols Plaza | 2020-01-09 | 0.052 | 0.052 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | McNicols Plaza | 2020-01-13 | 0.607 | 0.607 | Turned off sink and post appropriate signage | Turned off | 2020-01-21
Scranton School District | McNicols Plaza | 2020-01-20 | 0.0149 | 0.0149 | Turned off sink and post appropriate signage | Turned off | 2020-01-21
Scranton School District | McNicols Plaza | 2019-03-04 | 0.056 | 0.056 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | Northeast Intermediate | 2020-01-09 | 0.015 | 0.015 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | Northeast Intermediate | 2020-01-09 | 0.027 | 0.027 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | Northeast Intermediate | 2020-01-09 | 0.017 | 0.017 | Turned off sink and post appropriate signage | Turned off | 2020-01-09
Scranton School District | Northeast Intermediate | 2020-01-14 | 0.021 | 0.021 | Turned off sink and post appropriate signage | Appropriate signage | 2020-01-14
The School District of Philadelphia | Anderson Elementary School- Faucet/Tap Inside bathroom RM 105 | 2019-01-03 | 15.6 | 15.6 | Made handwash sink. Will apply sign. | N/A | 2019-01-03
The School District of Philadelphia | Anderson Elementary School- Faucet/Tap inside Room 102 | 2019-01-03 | 12.3 | 12.3 | Replaced faucet and retested. | 3,307 Permanently removed faucet | 2019-02-15
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 109 | 2019-06-27 | 161.5 | 161.5 | Made handwash sink. Applied sign. | N/A | 2019-06-27
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 104 | 2019-06-27 | 31.5 | 31.5 | Made handwash sink. Applied sign. | N/A | 2019-06-27
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 101 | 2019-06-28 | 26.4 | 26.4 | Made handwash sink. Applied sign. | N/A | 2019-06-28
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 218 | 2019-06-28 | 2281 | 2281 | Made handwash sink. Applied sign. | N/A | 2019-06-28
The School District of Philadelphia | Bethune Elementary School- Water fountain outside Room 215 | 2019-07-10 | 29.7 | 29.7 | Made handwash sink. Applied sign. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-10
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 220 (Right hall side wall) | 2019-06-28 | 139.2 | 139.2 | Made handwash sink. Applied sign. | N/A | 2019-06-28
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 220 (Left center hall side wall) | 2019-06-28 | 73.8 | 73.8 | Made handwash sink. Applied sign. | N/A | 2019-06-28
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 220 (Left hall wall side) | 2019-06-28 | 187.5 | 187.5 | Made handwash sink. Applied sign. | N/A | 2019-06-28
The School District of Philadelphia | Bethune Elementary School- Water fountain on sink in Room 111 | 2019-07-10 | 16.5 | 16.5 | Permanently removed bubble head. Applied sign on associated faucet. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-10
The School District of Philadelphia | Bethune Elementary School- Water fountain on sink in Room 112 | 2019-07-10 | 70.6 | 70.6 | Permanently removed bubble head. Applied sign on associated faucet. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-10
The School District of Philadelphia | Bethune Elementary School- Faucet/Tap in Room 217 | 2019-07-10 | 42.6 | 42.6 | Made handwash sink. Applied sign. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-10
The School District of Philadelphia | Bethune Elementary School- Water fountain outside Room 217 | 2019-07-10 | 23.9 | 23.9 | Replaced with Hydration Station. *Outlet was previously not in use and was only turned on for testing. | N/A | N/A
The School District of Philadelphia | Blaine Elementary School- Water fountain in Room 100 | 2019-07-02 | 180 | 180 | Water fountain shut off | N/A | 2019-07-02
The School District of Philadelphia | Blaine Elementary School- Water fountain outside Room 309 | 2019-07-24 | 35.1 | 35.1 | Water fountain shut off | N/A | 2019-07-24
The School District of Philadelphia | Blaine Elementary School- Faucet/Tap in Room 308 | 2019-07-24 | 206.6 | 206.6 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-24
The School District of Philadelphia | Bridesburg Elementary School- In kitchen right. | 2019-04-11 | 15.4 | 15.4 | Replaced faucet and retested. | 2.1 Returned to service | 2019-08-06
The School District of Philadelphia | Comegys Elementary School- Faucet in Room212 | 2019-01-24 | 222.2 | 222.2 | Replaced faucet and retested. | 68.5 Made handwash sink. Will apply sign. | 2019-02-22
The School District of Philadelphia | Comegys Elementary School- Water fountain outside Room 104. | 2019-01-24 | 17.2 | 17.2 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | Day Elementary School- Fountain in kitchen. | 2019-10-29 | 47.4 | 47.4 | Fountain shut off. | N/A | 2019-10-29
The School District of Philadelphia | Day Elementary School- Fountain in kitchen (right). | 2019-10-04 | 17.1 | 17.1 | Fountain shut off. | N/A | 2019-10-04
The School District of Philadelphia | William Dick Elementary School- Hydration Station outside boy's room. | 2019-05-29 | 41.1 | 41.1 | Replaced filter and retested. | <1.0 Returned to service. | 2019-10-03
The School District of Philadelphia | William Dick Elementary School- Foutain in Nurse's Restroom. | 2019-05-30 | 36.2 | 36.2 | Replaced faucet, removed screen, and retested. | 6.2 Returned to service. | 2019-10-03
The School District of Philadelphia | William Dick Elementary School- Fountain in Room 314. | 2019-05-30 | 30.9 | 30.9 | Made handwash sink. | N/A | 2019-05-30
The School District of Philadelphia | William Dick Elementary School- Water fountain outside Room 301. | 2019-05-30 | 356.6 | 356.6 | Permanently removed bubble head. | N/A | 2019-05-30
The School District of Philadelphia | Duckrey Elementary School- Faucet/Tap in Room 206. | 2019-06-11 | 409.6 | 409.6 | Made handwash sink. | N/A | 2019-06-11
The School District of Philadelphia | Duckrey Elementary School- Faucet/Tap in Room 214. | 2019-06-12 | 8768 | 8768 | Made handwash sink. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-12
The School District of Philadelphia | Duckrey Elementary School- Faucet/Tap in Room 218 (back of room right center). | 2019-06-11 | 668.4 | 668.4 | Made handwash sink. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-11
The School District of Philadelphia | Duckrey Elementary School- Water fountain in Room 222. | 2019-06-11 | 37.8 | 37.8 | Permanently removed bubble head. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-11
The School District of Philadelphia | Duckrey Elementary School- Faucet/Tap in Room 220 | 2019-06-12 | 47.7 | 47.7 | Made handwash sink. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-12
The School District of Philadelphia | Duckrey Elementary School- Faucet/Tap in Room 221 | 2019-06-12 | 879.4 | 879.4 | Made handwash sink. | N/A | 2019-06-12
The School District of Philadelphia | Edmonds Elementary School- Water fountain in lunchroom. | 2019-10-17 | 18.3 | 18.3 | Fountain shut off. | N/A | 2019-10-17
The School District of Philadelphia | Edmonds Elementary School- Water fountain outside 217A. | 2019-10-17 | 43.5 | 43.5 | Fountain shut off. | N/A | 2019-10-17
The School District of Philadelphia | Edmonds Elementary School- Faucet/Tap in Room 102. | 2019-10-17 | 17.8 | 17.8 | Faucet shut off. | N/A | 2019-10-17
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room B01 (front right). | 2019-04-17 | 200.4 | 200.4 | Made handwash sink. | N/A | 2019-04-17
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room B01 (front left). | 2019-04-17 | 33.2 | 33.2 | Made handwash sink. | N/A | 2019-04-17
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap In Room B01 (back left). | 2019-04-17 | 33 | 33 | Made handwash sink. | N/A | 2019-04-17
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room 205. | 2019-04-18 | 73.2 | 73.2 | Made handwash sink. | N/A | 2019-04-18
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room 203. | 2019-04-18 | 182.5 | 182.5 | Made handwash sink. | N/A | 2019-04-18
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room 213. | 2019-04-18 | 127.5 | 127.5 | Made handwash sink. | N/A | 2019-04-18
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room 217 (back wall). | 2019-04-18 | 70.2 | 70.2 | Made handwash sink. | N/A | 2019-04-18
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room 218. | 2019-04-18 | 17.5 | 17.5 | Made handwash sink. | N/A | 2019-04-18
The School District of Philadelphia | Elkin Elementary School- Faucet/Tap in Room 109. | 2019-04-18 | 411.4 | 411.4 | Made handwash sink. | N/A | 2019-04-18
The School District of Philadelphia | Hackett Elementary School- Water fountain in Room 112. | 2018-11-16 | 38.5 | 38.5 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | Hackett Elementary School- Faucet/Tap in copy room (main office). | 2018-11-16 | 17.1 | 17.1 | Replaced faucet and retested. | 22.7 Made handwash sink. Will apply sign. | 2019-02-14
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap in Room 303 | 2019-01-11 | 71.4 | 71.4 | Faucet shut off. | N/A | 2019-01-11
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap in Room 310 | 2019-01-11 | 381.4 | 381.4 | Faucet shut off. | N/A | 2019-01-11
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap in Room 334. | 2019-01-11 | 75.1 | 75.1 | Faucet shut off. | N/A | 2019-01-11
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap in Room 319. | 2019-01-11 | 26.9 | 26.9 | Faucet shut off. | N/A | 2019-01-11
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap in Room 302. | 2019-01-11 | 79.7 | 79.7 | Faucet shut off. | N/A | 2019-01-11
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap in Kitchen Room 109S (Left). | 2019-01-15 | 35.4 | 35.4 | Faucet shut off. | N/A | 2019-01-15
The School District of Philadelphia | Hamilton Elementary School- Faucet/Tap (health suite back office). | 2019-01-15 | 107.6 | 107.6 | Faucet shut off. | N/A | 2019-01-15
The School District of Philadelphia | Harrington School- Faucet/Tap in Room B03. | 2019-01-17 | 443.4 | 443.4 | Replaced faucet and retested. | 10.2 Made handwash sink. Will apply sign. | 2019-02-15
The School District of Philadelphia | Harrington School- Faucet/Tap in IMC office. | 2019-01-17 | 26.9 | 26.9 | Permanently removed faucet. | N/A | 2019-01-17
The School District of Philadelphia | Harrington School- Water fountain in Room 101. | 2019-01-17 | 16.7 | 16.7 | Replaced with Hydration Station. *Outlet was previously not in use and was only turned on for testing. | N/A | N/A
The School District of Philadelphia | Hartranft Elementary School- Water fountain in Room 115. | 2018-12-14 | 1538 | 1538 | Permanently removed bubble head. *Outlet was previously not in use and was only turned on for testing. | N/A | 2018-12-14
The School District of Philadelphia | Hartranft Elementary School- Water fountain in Room 116. | 2018-12-14 | 51.7 | 51.7 | Replaced with Hydration Station. *Outlet was previously not in use and was only turned on for testing. | N/A | N/A
The School District of Philadelphia | Hartranft Elementary School- Water fountain in Room 117. | 2018-12-14 | 678.5 | 678.5 | Replaced with Hydration Station. *Outlet was previously not in use and was only turned on for testing. | N/A | N/A
The School District of Philadelphia | Hartranft Elementary School- Water fountain in Room 118. | 2018-12-14 | 40.2 | 40.2 | Permanently removed bubble head. *Outlet was previously not in use and was only turned on for testing. | N/A | 2018-12-14
The School District of Philadelphia | Hartranft Elementary School- Water fountain across from Room 121. | 2018-12-14 | 282.2 | 282.2 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | Hartranft Elementary School- Water fountain across from Room 202. | 2018-12-14 | 35.4 | 35.4 | Permanently removed bubble head. | N/A | 2018-12-14
The School District of Philadelphia | Hartranft Elementary School- Water fountain across from Room 213. | 2018-12-14 | 19.2 | 19.2 | Permanently removed bubble head. | N/A | 2018-12-14
The School District of Philadelphia | Hartranft Elementary School- Faucet/Tap kitchen prep island. | 2018-12-14 | 17.9 | 17.9 | Flushing protocol implemented by food services. All water outlets used daily should be flushed for 15 minutes daily before use. Those not used daily must be flushed for 30 minutes prior to use. | N/A | 2018-12-14
The School District of Philadelphia | Hopkinson Elementary School- Faucet/Tap in Room 103. | 2019-03-22 | 1633 | 1633 | Faucet shut off. | N/A | 2019-03-22
The School District of Philadelphia | Hunter Elementary School- Water fountain in sink in Room 101A. | 2019-02-08 | 16.2 | 16.2 | Fountain shut off. | N/A | 2019-02-08
The School District of Philadelphia | Hunter Elementary School- Water fountain in sink in Room 101C. | 2019-02-08 | 31.5 | 31.5 | Fountain shut off. | N/A | 2019-02-08
The School District of Philadelphia | Hunter Elementary School- Faucet/Tap inside Room 101C. | 2019-02-08 | 28.6 | 28.6 | Fountain shut off. | N/A | 2019-02-08
The School District of Philadelphia | Hunter Elementary School- Faucet/Tap inside Room 101E. | 2019-02-08 | 18.3 | 18.3 | Faucet shut off. | N/A | 2019-02-08
The School District of Philadelphia | Hunter Elementary School- Faucet/Tap in Room 207. | 2019-02-08 | 52.4 | 52.4 | Faucet shut off. | N/A | 2019-02-08
The School District of Philadelphia | Juniata Park Academy- Pot filler in kitchen next to oven. | 2019-03-13 | 152.9 | 152.9 | Flushing protocol implemented by food services. All water outlets used daily should be flushed for 15 minutes daily before use. Those not used daily must be flushed for 30 minutes prior to use. | N/A | 2019-03-13
The School District of Philadelphia | Juniata Park Academy- In kitchen by pot washer left. | 2019-03-13 | 35.7 | 35.7 | Flushing protocol implemented by food services. All water outlets used daily should be flushed for 15 minutes daily before use. Those not used daily must be flushed for 30 minutes prior to use. | N/A | 2019-03-13
The School District of Philadelphia | Juniata Park Academy- In kitchen by steamer. | 2019-03-14 | 47.6 | 47 | Flushing protocol implemented by food services. All water outlets used daily should be flushed for 15 minutes daily before use. Those not used daily must be flushed for 30 minutes prior to use. | N/A | 2019-03-14
The School District of Philadelphia | Juniata Park Academy- Faucet/Tap in Room 110. | 2019-03-14 | 47.9 | 47.9 | Made hand wash sink only. Will apply signage. | N/A | 2019-03-14
The School District of Philadelphia | Juniata Park Academy- Faucet/Tap in Room 108. | 2019-03-14 | 24 | 24 | Made hand wash sink only. Will apply signage. | N/A | 2019-03-14
The School District of Philadelphia | Juniata Park Academy- Faucet/Tap in Room 113. | 2019-03-15 | 18 | 18 | Made hand wash sink only. Will apply signage. | N/A | 2019-03-15
The School District of Philadelphia | W.D. Kelley Elementary- Faucet/Tap in Room 109. | 2019-10-11 | 229.4 | 229.4 | Faucet shut off. | N/A | 2019-10-11
The School District of Philadelphia | Kenderton Elementary School- Faucet/Tap in kitchen (back wall right). | 2019-07-12 | 26.7 | 26.7 | Faucet shut off. | N/A | 2019-07-12
The School District of Philadelphia | Kenderton Elementary School- Faucet/Tap in nurses outer office. | 2019-07-12 | 42.4 | 42.4 | Faucet shut off. | N/A | 2019-07-12
The School District of Philadelphia | Kenderton Elementary School- Water fountain outside Room 206. | 2019-07-12 | 19.9 | 19.9 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-12
The School District of Philadelphia | Kenderton Elementary School- Faucet/Tap Room 100 (teachers lounge between washer and dryer). | 2019-07-17 | 940 | 940 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-17
The School District of Philadelphia | Logan Elementary School- Outside boy's room. | 2019-10-24 | 17.8 | 17.8 | Outlet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-10-24
The School District of Philadelphia | Logan Elementary School- Water fountain in Room 104. | 2019-10-24 | 43.5 | 43.5 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-10-24
The School District of Philadelphia | Logan Elementary School- Water fountain in Room 108. | 2019-10-24 | 24.6 | 24.6 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-10-24
The School District of Philadelphia | Logan Elementary School- Faucet/Tap in speech and language room. | 2019-10-24 | 4326 | 4326 | Faucet shut off. | N/A | 2019-10-24
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 320. | 2019-01-09 | 113.4 | 113.4 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 309. | 2019-01-09 | 22.1 | 22.1 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 311. | 2019-01-09 | 197.4 | 197.4 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 319. | 2019-01-09 | 15.9 | 15.9 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 313 | 2019-01-09 | 35.3 | 35.3 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 200B. | 2019-01-09 | 93.2 | 93.2 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 212. | 2019-01-09 | 166.2 | 166.2 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Water fountain outside Room 103. | 2019-01-09 | 42.9 | 42.9 | Fountain shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 100D. | 2019-01-09 | 35.3 | 35.3 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 104. | 2019-01-09 | 21.3 | 21.3 | Faucet shut off. | N/A | 2019-01-09
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Room 106 (left far side). | 2019-01-10 | 66.6 | 66.6 | Faucet shut off. | N/A | 2019-01-10
The School District of Philadelphia | Longstreth Elementary School- Fountain/Tap in Room 110D nurse's office. | 2019-01-10 | 42.6 | 42.6 | Faucet shut off. | N/A | 2019-01-10
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in kitchen (left). | 2019-01-10 | 53.3 | 53.3 | Faucet shut off. | N/A | 2019-01-10
The School District of Philadelphia | Longstreth Elementary School- Faucet/Tap in Kitchen (right). | 2019-01-10 | 81.5 | 81.5 | Faucet shut off. | N/A | 2019-01-10
The School District of Philadelphia | Moffet Elementary School- Water fountain (in sink in Room 216). | 2018-11-21 | 16.9 | 16.9 | Fountain shut off. | N/A | 2018-11-21
The School District of Philadelphia | Moffet Elementary School- Water fountain (around corner from Room 221) | 2018-11-21 | 25.5 | 25.5 | Fountain shut off. | N/A | 2018-11-21
The School District of Philadelphia | Moffet Elementary School- Water fountan (in sink in Room 205). | 2018-11-21 | 17.8 | 17.8 | Fountain shut off. | N/A | 2018-11-21
The School District of Philadelphia | Moffet Elementary School- Faucet/Tap in Nurses office 119A. | 2018-11-21 | 1754 | 1754 | Faucet shut off. | N/A | 2018-11-21
The School District of Philadelphia | Morton Elementary School- Water fountain in Room 100. | 2019-02-07 | 62.2 | 62.2 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-02-07
The School District of Philadelphia | Morton Elementary School- Water fountain in café next to kitchen. | 2019-02-07 | 94.9 | 94.9 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-02-07
The School District of Philadelphia | Morton Elementary School- Water fountain in sink in Room 212. | 2019-02-07 | 44.5 | 44.5 | Fountain shut off. | N/A | 2019-02-07
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 211. | 2019-02-07 | 434.3 | 434.3 | Fountain shut off. | N/A | 2019-02-07
The School District of Philadelphia | Morton Elementary School- Water fountain in Room 206. | 2019-02-08 | 123.3 | 123.3 | Fountain shut off. | N/A | 2019-02-08
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 204. | 2019-02-07 | 258.9 | 258.9 | Fountain shut off. | N/A | 2019-02-07
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 203. | 2019-02-07 | 33.8 | 33.8 | Faucet shut off. | N/A | 2019-02-07
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 315. | 2019-02-08 | 25.5 | 25.5 | Faucet shut off. | N/A | 2019-02-08
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 320. | 2019-02-08 | 117.4 | 117.4 | Faucet shut off. | N/A | 2019-02-08
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 309. | 2019-02-08 | 27.4 | 27.4 | Faucet shut off. | N/A | 2019-02-08
The School District of Philadelphia | Morton Elementary School- Faucet/Tap in Room 300. | 2019-02-08 | 27.9 | 27.9 | Faucet shut off. | N/A | 2019-02-08
The School District of Philadelphia | Penn Alexander- Sink in kitchen on back wall. | 2018-12-04 | 18.1 | 18.1 | Removed screen and retested. | 19.4 Made hand wash sink only. Will apply signage. | 2019-01-16
The School District of Philadelphia | Penn Alexander- Sink in Rooom 108. | 2018-12-04 | 607.7 | 607.7 | Replaced the faucet and retested. | <1.00 | 2019-02-21
The School District of Philadelphia | Penn Alexander- Food prep sink in kitchen across from B05. | 2018-12-04 | 37.9 | 37.9 | Flushed and retested | 80 Flushing protocol implemented by food services. All water outlets used daily should be flushed for 15 minutes daily before use. Those not used daily must be flushed for 30 minutes prior to use. | 2019-01-16
The School District of Philadelphia | Penn Alexander- Food prep sink in kitchen back wall | 2018-12-04 | 30.2 | 30.2 | Flushed and retested | 8.7 Flushing protocol implemented by food services. All water outlets used daily should be flushed for 15 minutes daily before use. Those not used daily must be flushed for 30 minutes prior to use. | 2019-01-16
The School District of Philadelphia | Sheridan Elementary School- Water fountain in sink in Room 102. | 2019-04-30 | 22.2 | 22.2 | Permanently removed water fountain. Made adjacent sink handwash only and applied sign.*Outlet was previously not in use and was only turned on for testing. | N/A | 2019-04-30
The School District of Philadelphia | Sheridan Elementary School- Faucet/Tap in Room 310 (center). | 2019-04-30 | 78.5 | 78.5 | Made handwash sink. Applied sign. | N/A | 2019-04-30
The School District of Philadelphia | Sullivan Elementary School- Faucet/Tap in ice machine. | 2019-05-07 | 561.3 | 561.3 | Faucet shut off. | N/A | 2019-05-07
The School District of Philadelphia | Sullivan Elementary School- Water fountain in Room 110. | 2019-05-07 | 1407 | 1407 | Fountain shut off. | N/A | 2019-05-07
The School District of Philadelphia | Sullivan Elementary School- Water fountain in Room 103. | 2019-05-07 | 67.8 | 67.8 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-05-07
The School District of Philadelphia | Stearne Elementary School- Faucet/Tap in Room 307 | 2019-05-08 | 17 | 17 | Made handwash sink. Applied sign. | N/A | 2019-05-08
The School District of Philadelphia | Stearne Elementary School- Faucet/Tap in Room 305 | 2019-05-08 | 15.8 | 15.7 | Made handwash sink. Applied sign. | N/A | 2019-05-08
The School District of Philadelphia | Stearne Elementary School- Faucet/Tap inside Room 303 | 2019-05-09 | 74.3 | 74.3 | Made handwash sink. Applied sign. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-05-09
The School District of Philadelphia | Webster Elementary- Faucet/Tap in ice machine (office). | 2019-03-19 | 46.2 | 46.2 | Made handwash sink. Signage applied. | N/A | 2019-03-19
The School District of Philadelphia | Webster Elementary- Faucet/Tap in ice machine (material prep). | 2019-03-19 | 386.2 | 386.2 | Made handwash sink. Signage applied. | N/A | 2019-03-19
The School District of Philadelphia | Webster Elementary- Faucet/Tap in Room 209. | 2019-03-20 | 39.4 | 39.4 | Made handwash sink. Signage applied. | N/A | 2019-03-20
The School District of Philadelphia | Webster Elementary- Faucet/Tap in Room 200. | 2019-03-20 | 103.2 | 103.2 | Made handwash sink. Signage applied. | N/A | 2019-03-20
The School District of Philadelphia | Webster Elementary- Faucet/Tap in Room 312. | 2019-03-20 | 23.3 | 23.3 | Made handwash sink. Signage applied. | N/A | 2019-03-20
The School District of Philadelphia | Conwell Elementary School- Faucet/Tap in Room B1 | 2019-05-15 | 72.4 | 72.4 | Made handwash sink. Signage placed. | N/A | 2019-05-15
The School District of Philadelphia | Conwell Elementary School- Faucet/Tap in Room 104 (Annex- back wall right). | 2019-05-24 | 19 | 19 | Made handwash sign. Signage placed. | N/A | 2019-05-24
The School District of Philadelphia | Harding Middle School- Water fountain outside girl's side lunchroom left. | 2019-04-24 | 19.1 | 19.1 | Replaced with hydration station. | N/A | 2019-04-24
The School District of Philadelphia | Harding Middle School- Water fountain outside room 108. | 2019-05-14 | 28.9 | 28.9 | Permanently removed bubble head. | N/A | 2019-05-14
The School District of Philadelphia | Harding Middle School- Faucet/Tap in library office. | 2019-05-14 | 389.2 | 389.2 | Made handwash sink. | N/A | 2019-05-14
The School District of Philadelphia | Carver High School- Faucet/Tap in Room 145 (left). | 2019-06-06 | 22.7 | 22.7 | Faucet shut off. | N/A | 2019-06-06
The School District of Philadelphia | Carver High School- Faucet/Tap in Room 145 (right). | 2019-06-06 | 43.5 | 43.5 | Faucet shut off. | N/A | 2019-06-06
The School District of Philadelphia | Carver High School- Food prep in kitchen next to freezer. | 2019-06-06 | 299.8 | 299.8 | Outlet shut off. | N/A | 2019-06-06
The School District of Philadelphia | Carver High School- Water fountain outside Room 304 (left). | 2019-06-06 | 37.9 | 37.9 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-06
The School District of Philadelphia | Kensington Health & Sciences School- Faucet/Tap sink near mechanical closet in Room 216. | 2018-11-14 | 33.1 | 33.1 | Removed screen. Flushed. Retested. | 13.7 Made handwash sink. Will apply sign. | 2019-02-13
The School District of Philadelphia | Kensington Health & Sciences School- Faucet/Tap large faucet in first spit sink in Room 216. | 2018-11-14 | 41.7 | 41.7 | Removed screen. Flushed. Retested. | 12.7 Made handwash sink. Will apply sign. | 2019-02-13
The School District of Philadelphia | Kensington Health & Sciences School- Faucet/Tap fourth spit sink large faucet in Room 216. | 2018-11-14 | 375.2 | 375.2 | Removed screen. Flushed. Retested. | 103.1 Made handwash sink. Will apply sign. | 2019-02-13
The School District of Philadelphia | Kensington Health & Sciences School- Faucet/Tap sink in Room 214. | 2018-11-13 | 186.9 | 186.9 | Replaced faucet. Flushed Retested. | 18 Made handwash sink. Will apply sign. | 2019-02-13
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in Room 101. | 2019-07-18 | 100 | 100 | Faucet shut off. | N/A | 2019-07-18
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in Room 208 nurse's office. | 2019-07-18 | 31.6 | 31.6 | Faucet shut off. | N/A | 2019-07-18
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in nurse's restroom. | 2019-07-22 | 82.5 | 82.5 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-22
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in nurse's back office. | 2019-07-18 | 47 | 47 | Faucet shut off. | N/A | 2019-07-18
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in Room 226 front wall. | 2019-07-23 | 377.7 | 377.7 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-23
The School District of Philadelphia | Mastbaum High School. Faucet/Tap in Room 226 side wall left. | 2019-07-19 | 24.3 | 24.3 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-19
The School District of Philadelphia | Mastbaum High School. Faucet/Tap in Room 226 side wall center right. | 2019-07-19 | 74.4 | 74.4 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-19
The School District of Philadelphia | Mastbaum High School. Faucet/Tap in Room 226 side wall right. | 2019-07-19 | 20.1 | 20.1 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-19
The School District of Philadelphia | Mastbaum High School. Faucet/Tap in Room 226 on pillar door side. | 2019-07-19 | 22.5 | 22.5 | Faucet shut off. | N/A | 2019-07-19
The School District of Philadelphia | Mastbaum High School. Faucet/Tap in Room 226 teacher's desk. | 2019-07-19 | 34 | 34 | Faucet shut off. | N/A | 2019-07-19
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in Room 513 Culinary dining room. | 2019-07-19 | 23.1 | 23.1 | Faucet shut off. | N/A | 2019-07-19
The School District of Philadelphia | Mastbaum High School- Water fountain outside boys RM right. | 2019-07-22 | 15 | 15 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-07-22
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in room behind serving line in kitchen left. | 2019-07-22 | 22.7 | 22.7 | Faucet shut off. | N/A | 2019-07-22
The School District of Philadelphia | Mastbaum High School- Faucet/Tap in room behind serving line in kitchen right. | 2019-07-22 | 41.7 | 41.7 | Faucet shut off. | N/A | 2019-07-22
The School District of Philadelphia | Mastbaum High School- Faucet/Trap in kitchen side wall. | 2019-07-22 | 21.4 | 21.4 | Faucet shut off. | N/A | 2019-07-22
The School District of Philadelphia | Mastbaum High School- Water fountain outside room 306 right. | 2019-07-23 | 20.8 | 20.8 | Fountain shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 7/23/019
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 306. | 2018-12-13 | 22.5 | 22.5 | Faucet shut off. | Made handwash sink. Will apply sign. | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 318. | 2018-12-13 | 99.6 | 99.6 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | Made handwash sink. Will apply sign. | 2018-12-13
The School District of Philadelphia | Motivation High School- Water fountain outside Room 206 right. | 2018-12-13 | 18.8 | 18.8 | Permanently removed water fountain. *Outlet was previously not in use and was only turned on for testing. | N/A | 2018-12-13
The School District of Philadelphia | Motivation High School- Water fountain outside Room 206 left. | 2019-12-13 | 17.7 | 17.7 | Replaced with Hydration Station. *Outlet was previously not in use and was only turned on for testing. | N/A | N/A
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 200 right. | 2018-12-13 | 123.2 | 123.2 | Faucet shut off. | Made handwash sink. Will apply sign. | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 200 left. | 2018-12-13 | 17.6 | 17.6 | Faucet shut off. | Made handwash sink. Will apply sign. | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 200 prep room. | 2018-12-13 | 16.8 | 16.8 | Faucet shut off. | Made handwash sink. Will apply sign. | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap sink on left in Room 203. | 2018-12-13 | 49.6 | 49.6 | Faucet shut off. | Made handwash sink. Will apply sign. | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 209. | 2018-12-13 | 23.5 | 23.5 | Permanently removd faucet. *Outlet was previously not in use and was only turned on for testing. | N/A | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap in Room 221 | 2018-12-13 | 473.5 | 473.5 | Permanetly removed faucet. | N/A | 2018-12-13
The School District of Philadelphia | Motivation High School- Water fountain in lunchroom by candy machine. | 2018-12-13 | 20.1 | 20.1 | Permanently removed water fountain. | N/A | 2018-12-13
The School District of Philadelphia | Motivation High School- Faucet/Tap in nurse's office. | 2018-12-13 | 25.7 | 25.7 | Replaced faucet and retested. | 5.3 Returned to service. | 2019-02-28
The School District of Philadelphia | Penn Treaty High School- Water fountain outside Room 101. | 2018-10-30 | 20.8 | 20.8 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | Penn Treaty High School- Water fountain around corner from Room 214. | 2018-10-30 | 72.7 | 72.7 | Removed and capped off. | N/A | 2018-10-30
The School District of Philadelphia | Penn Treaty High School- Water fountain outside of Room 307. | 2018-10-30 | 51.2 | 51.2 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | Penn Treaty High School- Water fountain around corner from Room 319. | 2018-10-30 | 58.5 | 58.5 | Removed and capped off. | N/A | 2018-10-30
The School District of Philadelphia | Penn Treaty High School- Water fountain outside of Room 005. | 2018-10-30 | 107.4 | 107.4 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | Randolph High School- Faucet/Tap outside nurse's office in waiting room. | 2019-06-18 | 19.1 | 19.1 | Faucet shut off. | N/A | 2019-06-18
The School District of Philadelphia | Randolph High School- Faucet/Tap in Room 38 (back wall center). | 2019-06-19 | 15.4 | 15.4 | Faucet shut off. | N/A | 2019-06-19
The School District of Philadelphia | Randolph High School- Faucet/Tap In Room 38 by rear door. | 2019-06-19 | 32 | 32 | Faucet shut off. | N/A | 2019-06-19
The School District of Philadelphia | Randolph High School- Faucet/Tap in Room 38 (dark room). | 2019-06-19 | 33.5 | 33.5 | Faucet shut off. | N/A | 2019-06-19
The School District of Philadelphia | Randolph High School- Water fountain in welding shop outside boys BR. | 2019-06-20 | 26.2 | 26.2 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-20
The School District of Philadelphia | Randolph High School- Faucet/Tap in ice machine in office. | 2019-06-27 | 28.4 | 28.4 | Faucet shut off. *Outlet was previously not in use and was only turned on for testing. | N/A | 2019-06-27
The School District of Philadelphia | Sayre Middle School- Faucet/Tap in health clinic main room. | 2018-12-21 | 36.8 | 36.8 | *Outlet was previously not in use and was only turned on for testing. | Made handwash sink. Will apply sign. | 2018-12-21
The School District of Philadelphia | Sayre Middle School- Water fountain outside health suite left. | 2018-12-21 | 24.3 | 24.3 | *Outlet was previously not in use and was only turned on for testing. | Permanently removed fountain. | 2018-12-21
The School District of Philadelphia | Sayre Middle School-Water fountain outside health suite right. | 2018-12-21 | 130.8 | 130.8 | *Outlet was previously not in use and was only turned on for testing. | Permanently removed fountain. | 2018-12-21
The School District of Philadelphia | Sayre Middle School- Water fountain in lunchroom left. | 2019-01-03 | 15.3 | 15.3 | Replaced bubble head and retested. | 25 Permanently removed fountain | 2019-02-14
The School District of Philadelphia | Sayre Middle School- Water fountain in girl's gym. | 2019-01-03 | 48.8 | 48.8 | Permanently removed fountain. | N/A | 2019-01-03
The School District of Philadelphia | Sayre Middle School- Faucet/Tap in Room 115. | 2019-01-03 | 75.3 | 75.3 | Replaced faucet and retested. | 2.7 Made hand wash sink only. Will apply signage. | 2019-02-14
The School District of Philadelphia | U School at Ferguson- Water fountain inside 2nd floor main office. | 2018-11-28 | 46.6 | 46.6 | Replaced with Hydration Station. | N/A | N/A
The School District of Philadelphia | U School at Ferguson- Water fountain across from boys RM right. | 2018-11-28 | 54.1 | 54.1 | Removed and capped off. | N/A | 2018-11-28
Carbon Lehigh Intermediate Unit #21 | Carbon Learning and Achievement School-BS-9 | 2020-01-18 | 0 | 30 | Decommissioned | N/A | 2020-02-05
End of Fourth Quarterly Report
Governor Mifflin SD | Governor Mifflin High School | 2020-01-24 | 0 | 0.08 | Retest and sign placed that reads "do not drink water from this tap". | <0.001 | 2020-02-20
Pan American Academy Charter School | Pan American Academy Charter School | 2020-02-10 | <1 | 290 | Removed from Service | N/A | 2020-02-10
Pan American Academy Charter School | Pan American Academy Charter School | 2020-03-04 | <1 | 794 | Removed From Service | N/A | 2020-02-28
Central Bucks School District | Buckingham ES | 2019-06-12 | <1 | 449 | a pH adjustment system will be added, however that will not be installed until September 2020 (this was prior to Covid-19). In the meantime, bottled water was being provided. | N/A | N/A
Central Bucks School District | Cold Spring ES | 2019-06-12 | <1 | 15.2 | Replaced Fixture | 3.1 | 2019-08-13
Central Bucks School District | Kutz ES | 2019-06-06 | <1 | 25.7 | Replaced Fixtures | 5.9 | 2019-08-14
Central Bucks School District | Groveland ES | 2019-06-14 | <1 | 19.4 | Replaced Fixture | 12.5 | 2019-08-13
Central Bucks School District | Lenape ES | 2019-06-14 | <1 | 24.9 | One retest showed one of the fixtures to within an acceptable range. The other source was above so it was put out of service. | 1.8 for one of the sources | 2019-08-16
Central Bucks School District | Tohickon MS | 2019-06-14 | <1 | 17.6 | Replaced Fixture | 1.8 | 2019-08-16
Central Bucks School District | Unami MS | 2019-06-07 | <1 | 37.4 | Replaced Fixture | 1.2 | 2019-08-14
Central Bucks School District | East HS | 2019-06-12 | <1 | 20 | Removed Fountain | N/A | 2019-08-08
Central Bucks School District | West HS | 2019-06-13 | <1 | 85 | Removed Sink | N/A | 2019-08-08
Shikellamy School District | High School Stadium | 2018-12-07 | 0 | 0.076 | Replaced Hose Bib | N/A | 2019-01-11